Energized Electrical Work Permit

| To be completed by the electrically qualified persons doing the work |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building: | Room/Area: |  |  | Work Order # (if applicable) |  |
| Description of work to be done: |  |  |  |  |  |
| Description of Circuit/Equipment: |  |  |  |  |  |
| Justification for why equipment cannot be de-energized: |  |  |  |  |  |
| Results of Shock Hazard Analysis (NFPA-70E 2004 130.2) |  |  | Results of Arc Flash Hazard Analysis (NFPA-70E 2004 130.3) |  |  |
| Maximum Voltage: Glove Voltage Rating: Inspect gloves before use, check certification date |  |  | Risk Category: Flash Protection Boundary: (ft.) |  |  |
|  |  |  | All Natural Fiber Outerwear Fire Retardant Clothing Cal/cm2 ATPV Rating of garment: Required Additional PPE: |  | See NFPA Table 130.7(C) (11), Protective Clothing Characteristics on the last page of this permit. |
| Limited Approach Boundary: (ft.) Restricted Approach Boundary: (ft.) Prohibited Approach Boundary: (ft.) |  |  |  |  |  |
| Safety Checklist (Verify that proper controls are in place): |  |  |  |  |  |
| Workers must be trained, qualified, and have full knowledge of equipment. Insulated tools and equipment required. Remove all jewelry and metal apparel Means employed to restrict the access of unqualified persons from the work area. Documented job briefing including discussion of any job-specific hazards (e.g., NFPA-70E 2004 Annex I). See attachment for added information, special requirements, procedures, or written work plans. |  |  |  |  |  |
| Electrically Qualified Persons(s) that understand and agree to the above: |  |  |  |  |  |
| Printed or typed name(s): |  | Signature(s) |  |  | Date(s) |
| APPROVALS TO PERFORM THE WORK WHILE ELECTRICALLY ENERGIZED |  |  |  |  |  |
| Printed or typed name(s): |  | Signature(s) |  |  | Date(s) |
| Area Supervisor |  |  |  |  |  |
| Dean / Director |  |  |  |  |  |
| (check the one that applies) Contractor Electrical Supervisor (or) Department Faculty or Staff Qualified Supervisor (or) Facilities Management Electrical Supervisor |  |  |  |  |  |

NFPA 70E, Article 130, Table 130.7(C)(9)(a) Hazard/Risk Category Classifications

| Task (Assumes Equipment Is Energized, and Work Is Done Within the Flash Protection Boundary) | Hazard/ Risk Category | V-rated Gloves | V-rated Tools |
| --- | --- | --- | --- |
| Panelboards Rated 240 V and Below — Notes 1 and 3 |  |  |  |
| Circuit breaker (CB) or fused switch operation with covers on | 0 | N | N |
| CB or fused switch operation with covers off | 0 | N | N |
| Work on energized parts, including voltage testing | 1 | Y | Y |
| Remove/install CBs or fused switches | 1 | Y | Y |
| Removal of bolted covers (to expose bare, energized parts) | 1 | N | N |
| Opening hinged covers (to expose bare, energized parts) | 0 | N | N |
| Panelboards or Switchboards Rated >240 V and up to 600 V (with molded case or insulated case circuit breakers) — Notes 1 and 3 |  |  |  |
| CB or fused switch operation with covers on | 0 | N | N |
| CB or fused switch operation with covers off | 1 | N | N |
| Work on energized parts, including voltage testing | 2* | Y | Y |
| 600 V Class Motor Control Centers (MCCs) — Notes 2 (except as indicated) and 3 |  |  |  |
| CB or fused switch or starter operation with enclosure doors closed | 0 | N | N |
| Reading a panel meter while operating a meter switch | 0 | N | N |
| CB or fused switch or starter operation with enclosure doors open | 1 | N | N |
| Work on energized parts, including voltage testing | 2* | Y | Y |
| Work on control circuits with energized parts 120 V or below, exposed | 0 | Y | Y |
| Work on control circuits with energized parts >120 V, exposed | 2* | Y | Y |
| Insertion or removal of individual starter “buckets” from MCC — Note 4 | 3 | Y | N |
| Application of safety grounds, after voltage test | 2* | Y | N |
| Removal of bolted covers (to expose bare, energized parts) | 2* | N | N |
| Opening hinged covers (to expose bare, energized parts) | 1 | N | N |
| Note: V-rated Gloves are gloves rated and tested for the maximum line-to-line voltage upon which work will be done. V-rated Tools are tools rated and tested for the maximum line-to-line voltage upon which work will be done. 2* means that a double-layer switching hood and hearing protection are required for this task in addition to the other Hazard/Risk Category 2 requirements of Table 130.7(C)(10). Y = yes (required) N = no (not required) Notes: 1. 25 kA short circuit current available, 0.03 second (2 cycle) fault clearing time. 2. 65 kA short circuit current available, 0.03 second (2 cycle) fault clearing time. 3. For < 10 kA short circuit current available, the hazard/risk category required may be reduced by one number. 4. 65 kA short circuit current available, 0.33 second (20 cycle) fault clearing time. 5. 65 kA short circuit current available, up to 1.0 second (60 cycle) fault clearing time. 6. For < 25 kA short circuit current available, the hazard/risk category required may be reduced by one number. |  |  |  |
| NOTE: Also refer to NFPA Article 130, Table 130.7(C)(9)(a) Hazard/Risk Category Classifications for the following tasks. - 600 v Class Switchgear (with power circuit breakers or fused switches) - Other 600 V Class (277 V through 600 V, nominal) Equipment - NEMA E2 (fused contactor) Motor Starters, 2.3 kV though 7.2 kV - Metal Clad Switchgear, 1 kV and Above - Other Equipment 1 kV and Above |  |  |  |