|  | Facilities Management – Opening Electrical Panels Job Safety Analysis Form |
| --- | --- |

| Picture of task/equipment: |  | Task: | Opening Electrical Panels – Exposed Electrical Circuitry (for testing voltages and current) |  |
| --- | --- | --- | --- | --- |
|  |  | Name of Shop or Dept: | FM Electrical Shop |  |
|  |  | Job Title(s): | Electricians |  |
|  |  | Analyzed by: |  |  |
|  |  | Date: |  |  |
| Required PPE: |  |  |  |  |
| Cat 1-2-3 FRC/ FS/SG/GLV/HP/H/MI/HP/I |  |  |  |  |
| Required/Recommended Trainings: |  |  |  |  |
| Arc Flash, PPE, LOTO, First Aid- AED, Approach Boundary’s -- Limited /Restricted /Prohibited |  |  |  |  |
| TASK | HAZARDS |  |  | CONTROLS |
| Removing -Branch panel Cover 208V- 10/22kaic | Energized electrical circuits Electrical Shock Electrical Burn Arc Flash Bodily injury Pedestrian Traffic |  |  | Only Qualified Personnel to perform task PPE- Cat 1 Barricades/ Boundary’s Safety Person Cat IV Meter Be sure that Safety person Knows where to de-energize panel in the event of emergency |
| Removing -Branch panel Cover 480 V- 10/22kaic | Energized electrical circuits Electrical Shock Electrical Burn Arc Flash Bodily injury Pedestrian Traffic |  |  | Only Qualified Personnel to perform task PPE –Cat 2 Barricades/ Boundary’s Safety Person Cat IV Meter Be sure that Safety person Knows where to de-energize panel in the event of emergency |
| Removing –Distribution Board Cover 208-42Kaic | Energized electrical circuits Electrical Shock Electrical Burn Arc Flash Bodily injury Unauthorized Personnel |  |  | Only Qualified Personnel to perform task PPE- Cat1 Barricades/ Boundary’s Safety Person Cat IV Meter Be sure that Safety person Knows where to de-energize panel in the event of emergency |
| Removing –Distribution Board Cover 480V 42Kaic | Energized electrical circuits Electrical Shock Electrical Burn Arc Flash Bodily injury Unauthorized Personnel |  |  | Only Qualified Personnel to perform task PPE Cat2 Barricades/ Boundary’s Safety Person Cat IV Meter Be sure that Safety person Knows where to de-energize panel in the event of emergency |
| Removing- Rear Panels of Secondary Breakers 208V- 65KAic | Energized electrical circuits Electrical Shock Electrical Burn Arc Flash Bodily injury Unauthorized Personnel |  |  | Only Qualified Personnel to perform task PPE Cat 3 Barricades/ Boundary’s Safety Person Cat IV Meter Be sure that Safety person Knows where to de-energize panel in the event of emergency |
| Removing- Rear Panels of Secondary Breakers 480V- 65KAic | Energized electrical circuits Electrical Shock Electrical Burn Arc Flash Bodily injury Unauthorized Personnel |  |  | Only Qualified Personnel to perform task PPE Cat 3 Barricades/ Boundary’s Safety Person Cat IV Meter Be sure that Safety person Knows where to de-energize panel in the event of emergency |