|  | Job Safety Analysis |
| --- | --- |
|  | Facilities Services |  |  |
|  | Installation, Alteration, Maintenance, or Repair of High/Low Voltage Breakers |
|  | Notify personnel using the circuits to be interrupted in order to avoid potential injuries or interruption of research projects. Only qualified personnel, according to the Cal/OSHA definition, are permitted to perform these activities. Inspect tools and PPE prior to use. |
|  | Task | Hazards | Controls |
|  | Assess the accessibility of the panel | Injuries from the impact of doors adjacent to the panel or from foot/cart traffic | Post warning signs. Set up barriers. Use an assistant. |
|  |  | Trips or falls | Clear the access to the panel Clean up liquids under the panel. Lay down a non-conductive mat to avoid slippage. |
|  | 2. Remove the outer cover. | Foot or hand injury from handling the cover | Assistance with the panel cover Plan for the handling of the panel cover. |
|  |  | Muscle strain | Lift with the legs not the back. |
|  |  | Shock or electrocution | Watch the edges of the panel and be sure they don’t touch the wires in the panel box. |
|  | 3. Open the dead front. | Shock or electrocution | Visually inspect for condition of wires and other components. Locate the live components using a meter. Wear gloves properly insulated for the load of the panel. Use an insulation floor mat. If possible, reenergize the panel (if de-energized, the job is not “hot panel”) |
|  |  | Shock or electrocution | Watch the edges of the panel and be sure they don’t touch the wires in the panel box. |
|  | 4. Performing operations in the panel while energized | Shock and electrocution | Use the proper PPE in accordance with the supply voltage. Obtain assistance (watch) from a competent person trained in CPR. |
|  |  | Skin burns | Wear clothing that includes long sleeved shirt, long pants, and gloves, made of materials that do not increase the extent of injury from burning, and a face shield. |
|  |  | Eye burns and impact injuries from debris ejected during arc discharges | Wear goggles, appropriately darkened. |
|  | 5. Reassemble the panel. | All the hazards and controls for the previous tasks exist in reverse order. | Use the planning, engineering, and procedure controls for each of the tasks performed. |
|  |  | Shock or fire from the panel locks | Watch the position and location of the panel locks to assure they do not catch on a wore or other component while being replaced. |
|  | Required Training: 1. Work techniques and hazards involved in working on energized equipment | Required Personal Protective Equipment (PPE) PPE and tools that meet the provisions of ASTM specifications Gloves Eye protection Face shield Insulated mats Insulated tools |
| Other Information: |  |
| Contributors: |  |
| Created: | Month Year |
| JSA Library Number: |  |  |  |